## pricebid
Item Wise BoQ
BoQ_Ver3.1 | Item Wise |  | INR and Other Currency
Tender Inviting Authority: Purchase cum Stores Officer, NIPGR, New Delhi
Name of Work: Supply, Designing, Construction, Testing and Commissioning of DRR Facility at NIPGR, New Delhi.
Contract No: NIPGR/Engg./7/47/2021-22
Name of the Bidder/ Bidding Firm / Company :
PRICE SCHEDULE (This BOQ template must not be modified/replaced by the bidder and the same should be uploaded after filling the relevant columns, else the bidder is liable to be rejected for this tender. Bidders are allowed to enter the Bidder Name and Values only )
(This BOQ template must not be modified/replaced by the bidder and the same should be uploaded after filling the relevant columns, else the bidder is liable to be rejected for this tender. Bidders are allowed to enter the Bidder Name and Values only )
NUMBER # | TEXT # | NUMBER # | TEXT # | NUMBER # | NUMBER | NUMBER # | NUMBER # | NUMBER #
Sl. No. | Item Description | Quantity | Units | UNIT RATE In Figures To be entered by the Bidder in Rs. P | GST in Rs. P (Col. 5 x % of GST) | Total Unit Rate with GST (Col. 5+6) | TOTAL AMOUNT Without Taxes in Rs. P (Col. 3 x 5) | TOTAL AMOUNT With Taxes in Rs. P (Col. 3 x 7)
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9
Supply, Designing, Construction, Testing & Commissioning of DRR facility at NIPGR as per the Technical Specifications / Requirements attached with Technical Bid. Size of DRR facility should be 23 M x 7 M & 5 M x 4 M & Centre ht. 12 ft. & side ht. 9 ft. with following activities.
1 | Civil Work: Civil construction Standard* BL3-P Internal walls, ceilings, and floors resistant to liquids and chemicals. CC foundation .Curtain wall: 9” wide 600mm height above the DPC as per guidlines and Flooring / Moving Path between the Pits – Making of 4 Nos. Beds/Pits of 9m x 3m (4 nos.) & 4m x 3m (1 no.), 2m deep having a brick partition wall 2m below the ground level duly plastered and covered with waterproof cement slurry to avoid water movement among all the pits with brick beds. Disposal pit (Sump, size – 5’ x 4’ x 4) with individual collection pipes .all complete as per technical specifications enlclosed with tender and complete in all respect as per direction direction of Institute. | 1 | Job | 0 | 0 | 0 | 0 | 0
2 | RO, Storage Tank and Plumbing: rrigation by using UPVC pipes for individual pits fitted with agriculture-grade water flow control meters for monitoring and controlling of water flow to each pit (5 nos of flow meter; separate for each pit). Further, for the facility a precision/drip soil irrigation system. The customrised drip irrigation system should enable irrigating each plant and ensuring uniform irrigation in each plot area and the entire drip system network should be removable and re-laid for each crop season. Commercial RO unit (Esmartek ,Kent,Aqua make) having capacity of 200/Hr and separate Polymer storage tank of 2000 L capacity (Sintex / Purewell / Lotus) duly placed over a high-rise stable steel structure and concrete foundation.all complete as per technical specifications enlclosed with tender and complete in all respect as per direction direction of Institute. | 1 | Job | 0 | 0 | 0 | 0 | 0
3 | Structure and Cladding Work : The entire structure of the DRR facility should be constructed using a combination of ISI marked B class (Apollo make) (Zn coated) anti-corrosive, humidity-resistant galvanized tubular frames of 50mm x 50mm and 50mm x 25mm thickness. All the necessary joints of the structure should be made so as to prevent water seepage. All the fittings, clamps, screws and nuts should be GI plated to avoid corrosion. The structure should be made to endure wind speeds of at least 140 km/h. Just below the dome of the structure a false ceiling made of 6 mm double walled PC sheet should be installed. The area above the false ceiling should be equipped with an air modulation system and table & chairs etc all complete as per technical specifications elclosed with tender and complete in all respect as per direction direction of Institute. | 1 | Job | 0 | 0 | 0 | 0 | 0
4 | Air-conditioning, Cooling & Heating Work: Air management / HVAC System (Divided in Two separate Zones independent to each other ) AND ONE STAND BY UNIT.Air Handling Unit (Zeco/crystal/H. Tech): Double skin air handling unit ,Air cooled condensing unit of suitble capacity with scroll compressor with copper pipes etc all complete. Total cooling capacity 33TR (3 Units of 11 TR each). Ducting & Duct Insulation as well as the leak testing of ducts should be conducted as per applicable standards etc .all complete as per technical specifications elclosed with tender and complete in all respect as per direction direction of Institute. | 1 | Job | 0 | 0 | 0 | 0 | 0
5 | Lighting & Humidification Work: LIGHTING Facility should be illuminated with Photosynthetically Active Radiation LED Lamps to provide an average illumination of 300 µmoles/m2/s. Grow Lamps in addition to these Lamps Adjusting lights of variable wavelength s ho uld be provided with higher efficacies and higher photosynthetic photon flux along with Smart Digital Selectable Controlling of Color Spectrum. HUMIDIFICATION SYSTEM - DRR Facility should have an independent humidification system which gives non-wetting effects using ultrasonic humidifier having titanium coated ceramic discs duly clubbed with AHU for uniform maintenance of RH.etc all complete as per technical specifications elclosed with tender and complete in all respect as per direction direction of Institute. Temperature- 22-24 °C. RH – 60% ± 10%. Light - 300 µmoles/m2/s | 1 | Job | 0 | 0 | 0 | 0 | 0
6 | Controlling system : CONTROL PANEL (CPRI approved)- Microprocessor Control Panel for Automation (CE certified) Individual control for each parameter - Light, Temperature & Humidity. The control panel should be designed with the help of contractors and . Fully PLC/PID based control system for controlling and maintaining the desired Temperature, RH & Light for controlling the environment inside the facility along with data storage capacity on PLC itself. It should have a programming feature to link multiple programs and equipped with surge arresters, IP22 protection and TOUCH SCREEN CONTROLLER (HM) for depicting the values of Temperature, Humidity & Light of all probes. Control system will have audio/ 5 audio visual warning/alarm when set temperature/RH/ lighting is below or above the set values. Locking facility for the entire control system, along with two keys will be provided. No data loss, Option will be provided to send emails directly from the PLC with PC etc all complete as per technical specifications enlclosed with tender and complete in all respect as per direction direction of Institute.. | 1 | Job | 0 | 0 | 0 | 0 | 0
7 | Electrical Work inside the facility : Supply & Installations ofthree numbers of 32 Amp industrial sockets (L&T & Havells make). The room should be equipped with standard lighting, and cooling arrangements h lighting (Full spectrum LED grow lights (Fluortronix/Nexcel) suitable for plant growth providing the intensity of 220µmoles/m2/s) and one number of sink, one 32 Amp industrial socket, an electrical supply point (3-4 switch boxes and socket) for running the common lab instruments. etc all complete as per technical specifications enlclosed with tender and complete in all respect as per direction direction of Institute. | 1 | Job | 0 | 0 | 0 | 0 | 0
8 | External electrical power cable/panel with laying: DRR facility requires supply of 50 KW uninterrupted power. This need to be arranged from a main power panel located at distance measured at site. Mention a line about specifications for cable and panel and their makes. This include laying of electrical cable and erecting the panel at the site of the facility for drawing power for the facility..etc all complete as per technical specifications elclosed with tender and complete in all respect as per direction direction of Institute | 1 | Job | 0 | 0 | 0 | 0 | 0
9 | hermal and RGB imaging system: IMAGING SYSTEMS AND STRUCTURE: 1) High-performance RGB camera for chickpea root imaging 32.5 Megapixel, DIGIC 8 image processor with CMOS (APS-C) sensor, High-speed continuous shooting (of up to 10 fps), 4K UHD 30P/ Full HD 120P video, high sensitivity for high ISO capture with reduced noise, DIGIC 8 image processor, Built-in Wi-Fi and Bluetooth Technology. 3.0-inch Vari-angle Touch Screen LCD, Dual Pixel CMOS AF. 2) The imaging system for plot area should comprise of a RGB and a thermal imaging unit. The unit should facilitate synchronous capturing of RGB and thermal images of chickpea plantsunder controlled environmental conditions of greenhouse.For imaging of the mini-plots, Camera Track Slider Stabilizer Rail arrangement with camera Holding Kit, LED light, camera slider cart taking cinematic curve and pan shots should be provided all along the length and breadth of the DRR Facility for capturing the images i) RGB imaging camera ii) Thermal imaging camera iii)Associated accessory All specicifications of camers & accessaries are as per tehcnical specification enclosed with tender etc.complete in all respect as per direction direction of Institute.. | 1 | Job | 0 | 0 | 0 | 0 | 0
Total in figures | [6 empty] | 0 | 0
Quoted Rate in Words
| Purchase cum Stores Officer |  |  |  | Seal & Signature of Contractor