## pricebid
Item Wise BoQ
BoQ_Ver3.1 | Item Wise |  | INR and Other Currency
Tender Inviting Authority: Purchase cum Stores Officer, NIPGR, New Delhi
Name of Work: Supply, Installation, Testing & Commissioning of Electrical Facilities and Civil Infrastructure for Computational Network Infrastructure at NIPGR Campus, New Delhi.
Contract No: NIPGR/Engg./7/48/2022-23
Name of the Bidder/ Bidding Firm / Company :
(This BOQ template must not be modified/replaced by the bidder and the same should be uploaded after filling the relevant columns, else the bidder is liable to be rejected for this tender. Bidders are allowed to enter the Bidder Name and Values only )
NUMBER # | TEXT # | NUMBER # | TEXT # | NUMBER # | NUMBER | NUMBER # | NUMBER # | NUMBER #
Sl. No. | Item Description | Qty. | Units | UNIT RATE In Figures To be entered by the Bidder in Rs. P | GST in Rs. P (Col. 5 x % of GST) | Total Unit Rate with GST (Col. 5+6) | TOTAL AMOUNT Without Taxes in Rs. P (Col. 3 x 5) | TOTAL AMOUNT With Taxes in Rs. P (Col. 3 x 7)
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9
Civil work (Part-A)
1 | Providing and fixing tiled false ceiling of specified materials of size 595x595 mm in true horizontal level, suspended on inter locking metal grid of hot dipped galvanized steel sections ( galvanized @ 120 grams/ sqm, both side inclusive) consisting of main "T" runner with suitably spaced joints to get required length and of size 24x38 mm made from 0.30 mm thick (minimum) sheet, spaced at 1200 mm center to center and cross "T" of size 24x25 mm made of 0.30 mm thick (minimum) sheet, 1200 mm long spaced between main "T" at 600 mm center to center to form a grid of 1200x600 mm and secondary cross "T" of length 600 mm and size 24x25 mm made of 0.30 mm thick (minimum) sheet to be interlocked at middle of the 1200x600 mm panel to form grids of 600x600 mm and wall angle of size 24x24x0.3 mm and laying false ceiling tiles of approved texture in the grid including, required cutting/making, opening for services like diffusers, grills, light fittings, fixtures, smoke detectors etc. Main "T" runners to be suspended from ceiling using GI slotted cleats of size 27 x 37 x 25 x1.6 mm fixed to ceiling with 12.5 mm dia and 50 mm long dash fasteners, 4 mm GI adjustable rods with galvanised butterfly level clips of size 85 x 30 x 0.8 mm spaced at 1200 mm center to center along main T, bottom exposed width of 24 mm of all T-sections shall be pre-painted with polyester paint, all complete for all heights as per specifications, drawings and as directed by Engineer-in-charge
1a) | GI Metal Ceiling Lay in plain Tegular edge Global white color tiles of size 595x595 mm, and 0.5 mm thick with 8 mm drop; made of G I sheet having galvanizing of 100 gms/sqm (both sides inclusive) and electro statically polyester powder coated of thickness 60 microns (minimum), including factory painted after bending. | 150 | Sq.m | 0 | 0 | 0 | 0 | 0
2 | Providing and fixing aluminium work for doors, windows, ventilators and partitions with extruded built up standard tubular sections 2.5"x1.5" and 16 gauge and other sections of approved make conforming to IS: 733 and IS: 1285, fixing with dash fasteners of required dia and size, including necessary filling up the gaps at junctions, i.e. at top, bottom and sides with required EPDM rubber/ neoprene gasket etc. Aluminium sections shall be smooth, rust free, straight, mitered and jointed mechanically wherever required including cleat angle, Aluminium snap beading for glazing / paneling, C.P. brass / stainless steel screws, all complete as per architectural drawings. (Glazing, paneling and dash fasteners included) : All complete as per direction of Institute.
2a) | Polyster Powder coated aluminium (minimum thickness of powder coating 50 micron): With toughened tinted glass panes of 5 mm thickness. The partition or door will be partly filled with ACP(aluminium composite panel) 6mm thick and 5 mm thick glazing. All complete | 345 | Sqft. | 0 | 0 | 0 | 0 | 0
3a) | Providing and fixing aluminium die cast body tubular type universal hydraulic door closer (having brand logo with ISI, IS : 3564, embossed on the body, door weight upto 35 kg and door width upto 700 mm), with necessary accessories and screws etc. complete. | 2 | Each | 0 | 0 | 0 | 0 | 0
3b) | Providing and fixing aluminium tower bolts, ISI marked, anodised (anodic coating not less than grade AC 10 as per IS : 1868 ) transparent or dyed to required colour or shade, with necessary screws etc. complete
| 200mm x10mm | 4 | Each | 0 | 0 | 0 | 0 | 0
3c) | Providing and fxing of D- type SS Door handles of 300mm long and 19mm dia.all complete in required colour or shade with necessary Screws as per direction of Institute. | 4 | Each | 0 | 0 | 0 | 0 | 0
3d) | Providing and fixing bright finished 100 mm mortice lock with 6 levers without pair of handles of approved quality for aluminium door, with necessary screws etc complete as per direction of Engineer- in-charge. | 2 | Each | 0 | 0 | 0 | 0 | 0
3e) | Providing and fixing 150 mm bright finished floor brass door stopper with rubber cushion, necessary brass screws etc. to suit shutter thickness complete | 2 | Each | 0 | 0 | 0 | 0 | 0
4 | Providing and applying in position Antifungal & antibacterials Coating (Epoxy/PU) on the wall surface after necessary surface preparation and compatible putty of desired shade and colour of M/s FORSROC. | 220 | sqm | 0 | 0 | 0 | 0 | 0
5 | Providing and applying white cement based wall care putty of average minimum 2 mm thickness approved brand and manufacturer over the old painted wall after preape the surface even and smooth all complete | 220 | sqm | 0 | 0 | 0 | 0 | 0
Total in figures (Part - A) | [6 empty] | 0 | 0
Electrical work (Part-B):
1 | Supply, laying, testing & commissioning of 1100 volt grade armoured PVC insulated and sheathed aluminium conductor cable of 3.5C x 120 sqmm size on existing cable trays or MS clamp or in raceways complete as per CPWD specifications & instructions of Engineer in Charge. | 70 | Rmt. | 0 | 0 | 0 | 0 | 0
2 | Supplying and installing of size 100 mm width X 50 mm depth X 1.6 mm thickness of perforated pre-painted M.S. cable trays with perforation not more than 17.5%, in convenient sections, joined with connectors, suspended from the ceiling with M.S. suspenders including bolts & nuts, bends, tees, reducers painting suspenders etc as required & instructions of Engineer in Charge. | 40 | Rmt. | 0 | 0 | 0 | 0 | 0
3 | Supplying and making end termination with brass compression gland and aluminium lugs for cable of 3.5C x 120sqmm size of PVC insulated and PVC sheathed / XLPE aluminium conductor cable of 1.1 KV grade as required & instructions of Engineer in Charge. | 4 | Each | 0 | 0 | 0 | 0 | 0
4 | Supply, laying, testing & commissioning of 1100 volt grade flexible PVC insulated and sheathed copper conductor cable of 4C x 16 sqmm size on cable trays or in raceways complete as per CPWD specifications & instructions of Engineer in Charge. | 135 | Rmt. | 0 | 0 | 0 | 0 | 0
5 | Supplying and making end termination with PVC gland and copper lugs for 4C x 16 sqmm size PVC insulated and PVC sheathed / XLPE copper conductor cable of 1.1 KV grade as required & instructions of Engineer in Charge. | 16 | Each | 0 | 0 | 0 | 0 | 0
6 | Providing and fixing 250 amp TP MCCB rating and 25KA breaking capacity and triple pole MCCB in a MCCB enclosure including drilling holes in cubicle panel, making connections, etc. as required & instructions of Engineer in Charge.. | 1 | Each | 0 | 0 | 0 | 0 | 0
7 | Main Distribution Board
Design, manufacurer, testing at works & supply, installation, testing and commissioning of the following front operated front access 2mm thick sheet steel fabricated cubical type panel dust and vermin proof, complete with hinged and locable doors, detachable top cover, complete with interconnections by copper tapes/wires, painting, copper crimping lugs, brass glands, bonding to earth and epoxy painting, suitable for use at 415 volts, 3 phase 4 wire 50Hz system all as per IS, specifications and instructions of E.I.C.
All live accessible parts shall be shrouded and all equipments shall be finger tough proof. The bus bar insulation shall be with heat shrinkable sleeves. SMC/DMC busbar supports shall be used. Padlocking facility shall be provided.
1. Necessary gaskets for doors, flexible earthing, danger board etc., to be provided.
2. Gland plate shall be 3mm thick with knock outs.
INCOMING
1 no. 250 amp TP MCCB of 25KA service breaking capacity and trip setting as required, with over current and magnetic short circuit releases and heavy duty solid neutral link.
Indicating panel
The indicating panel of the incomer shall be provided with the following:
Digital ammeter of required range, CT's, Voltmeter.
3 Nos. phase indicating lamp; backed up with MCB
2 Nos. ON/OFF indicating lamp on incomer feeder for indicating the status of feeder.
Bus Bar
Electrolytic high conductivity aluminium three phase and neutral busbar rated at 250 amps having a maximum current density of 1 amp per sqmm. The neutral busbar is to be of 100% capacity.
OUTGOINGS
| 13 no. 63 amp 4P MCB of 10KA service breaking capacity, with over current and magnetic short circuit releases and heavy duty solid neutral link. | 1 | Each | 0 | 0 | 0 | 0 | 0
8 | Supplying and fixing 8 way (4 + 24), Double door, horizontal type three pole and neutral, sheet steel, MCB distribution board, 415 V, on surface/ recess, complete with tinned copper bus bar, neutral bus bar, earth bar, din bar, interconnections, powder painted including earthing etc. as required. (But without MCB/RCCB/Isolator | 6 | Each | 0 | 0 | 0 | 0 | 0
| Supplying and fixing of 8 way (4 + 24), Double doo Double doo surface/ recess mounting, vertical type, 415 V, TPN MCB distribution board of sheet steel, dust protected, duly powder painted, inclusive of 200 A tinned copper bus bar, common neutral link, earth bar, din bar for mounting MCBs (but without MCBs and incomer ) as required | 3 | Each | 0 | 0 | 0 | 0 | 0
9 | Supplying and fixing 20 amps rating, 240/415 volts, "C"curve, miniature circuit breaker suitable for inductive load of single poles in the existing MCB DB complete with connections,testing and commissioning etc. as required & instructions of Engineer in Charge. | 25 | Each | 0 | 0 | 0 | 0 | 0
10 | Supplying and fixing of 32 amps rating, 240/415 volts, "C"curve, miniature circuit breaker suitable for inductive load of Triple pole and neutral in the existing MCB DB complete with connections,testing and commissioning etc. as required & instructions of Engineer in Charge. | 12 | Each | 0 | 0 | 0 | 0 | 0
11 | Supplying and fixing 63 amp, four pole, 415 volts, isolator in the existing MCB DB complete with connections, testing and commissioning etc. as required & instructions of Engineer in Charge. | 15 | Each | 0 | 0 | 0 | 0 | 0
12 | Supplying and fixing single pole blanking plate in the existing MCB DB complete etc. as required & instructions of Engineer in Charge. | 20 | Each | 0 | 0 | 0 | 0 | 0
13 | Supplying and fixing of 100mm x 50mm, 1.2mm thick, PVC raceway with locking arrangement, 1.8mm thick push-fit joints including the cost of all accessories for PVC raceway such as couplers, endcaps,bends, tees, nut & bolts, washers,PVC gitti, SS screws,elbows, internal / external angles, junction boxes of required ways of the same make required and drilling, offwhite colour etc. complete as per specifications, getting it approved and as required and & instructions of Engineer in Charge. | 30 | Rmt. | 0 | 0 | 0 | 0 | 0
14 | Wiring for power plug with 2X4 sq. mm FRLS PVC insulated copper conductor single core cable in existing surface/ recessed steel conduit/steel raceway on wall alongwith 1 No 4 sq. mm FRLS PVC insulated copper conductor single core cable for earthing including end termination with sitable size of Cu. thimble complete as required and instruction of E.I.C | 295 | Rmt. | 0 | 0 | 0 | 0 | 0
15 | Supplying and fixing suitable size GI/PVC box with modular plate and cover in front on surface or in recess or on steel/PVC raceway, including providing and fixing 6 pin 5/6 & 15/16 amps modular universal socket outlet and 15/16amps modular switch, cutting of steel raceway cover, connection,testing etc. complete as required and instruction of E.I.C | 25 | Each | 0 | 0 | 0 | 0 | 0
16 | Earthing with G.I. earth pipe 4.5 metre long, 40 mm dia laid in hard soil including accessories, and providing masonry enclosure with cover plate having locking arrangement and watering pipe with funnel complete etc. including digging ground 4.5m x 1m x 1.5m deep and filling with soft soil and with alternate layers of salt and charcoal complete as required as required as per CPWD specifications & instructions of Engineer in Charge. | 2 | Each | 0 | 0 | 0 | 0 | 0
17 | Providing and fixing 25 mm X 5 mm G.I. strip on surface or in recess and connections etc. as required & instructions of Engineer in Charge. | 30 | Rmt. | 0 | 0 | 0 | 0 | 0
Total in figures (Part - B) | [6 empty] | 0 | 0
GRAND TOTAL (Part-A + Part-B) =
| Purchase cum Stores Officer |  |  |  | Seal & Signature of Contractor