## Sheet1
Item Wise BoQ
BoQ_Ver3.1 | Item Wise |  | INR and Other Currency
Tender Inviting Authority: Consultant Engineer, NIPGR, New Delhi
Name of Work: Replacement of Chilled water tank (make up / Expansion Tank) for supplying make up water to the chilled water line installed for old lab block.
Contract No: NIPGR/Engg./5/6(1)/2023-24
Name of the Bidder/ Bidding Firm / Company :
PRICE SCHEDULE (This BOQ template must not be modified/replaced by the bidder and the same should be uploaded after filling the relevant columns, else the bidder is liable to be rejected for this tender. Bidders are allowed to enter the Bidder Name and Values only )
(This BOQ template must not be modified/replaced by the bidder and the same should be uploaded after filling the relevant columns, else the bidder is liable to be rejected for this tender. Bidders are allowed to enter the Bidder Name and Values only )
NUMBER # | TEXT # | NUMBER # | TEXT # | NUMBER # | NUMBER | NUMBER # | NUMBER # | NUMBER #
Sl. No. | Item Description | Quantity | Units | UNIT RATE In Figures To be entered by the Bidder in Rs. P | GST in Rs. P (Col. 5 x % of GST) | Total Unit Rate with GST (Col. 5+6) | TOTAL AMOUNT Without Taxes in Rs. P (Col. 3 x 5) | TOTAL AMOUNT With Taxes in Rs. P (Col. 3 x 7)
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9
Expansion Tank (MS-1000 Ltr.)-2 Nos.
1 | Providing and placing on terrace (at all floor levels) fabricated out of MS Sheet, waterstorage tank, with cover and suitable locking arrangement and making necessary holes for inlet, outlet and overflow pipes with complete fittings and the civil base support for tank and legs grouted in the civil foundation . | 2 | No. | 0 | 0 | 0 | 0 | 0
Make: Sintex/J.S. Polyplast/Polycon
Expansion Tank Insulation(25 mm thick)
2 | Supplying , installation, testing & commissioning of external thermal insulation on tank with Duly laminated aluminum foil of mat finish closed cell elastometric nitrile rubber of minimum 45 Kg / cu m density, thermal conductivity 0.037 W/MK or better at 20 deg mean temperature class 'O' insulation applied by suitable adhesive complete including repairing of damage to building etc. as per specifications and as required complete in all respect.. The insulation material shall be fire rated for Class 1 as per BS 476 Part 6 : 1989 for fire propagation test and for Class 0 as per BS 476 Part 7, 1987 for surface spread of flame test. Water vapour permeability shall be not less than 0.024 per inch (2.48 x 10-14 Kg/m.s.Pa i.e. µ>7000: Water vapour diffusion resistance).The Material shall have Fire Approval from CBRI | 2 | No. | 0 | 0 | 0 | 0 | 0
Make: Armaflex/K -Flex/Supreme
Scope of Work
Dismantling of existing Tank along with accessories.
SITC of New tank as per existing installations complete with all accessories
Total in figures | [6 empty] | 0 | 0
Quoted Rate in Words
| Consultant Engineer |  |  |  | Seal & Signature of Contractor