## pricebid
Item Wise BoQ
BoQ_Ver3.1 | Item Wise |  | INR and Other Currency
Tender Inviting Authority: Consultant Engineer, NIPGR, New Delhi
Name of Work: Supply & Installation of electrical, furniture requirements & flooring, etc., at HRD Conference Room at NIPGR Campus, New Delhi.
Contract No: NIPGR/Engg./7/11/2023-24
Name of the Bidder/ Bidding Firm / Company :
PRICE SCHEDULE (This BOQ template must not be modified/replaced by the bidder and the same should be uploaded after filling the relevant columns, else the bidder is liable to be rejected for this tender. Bidders are allowed to enter the Bidder Name and Values only )
(This BOQ template must not be modified/replaced by the bidder and the same should be uploaded after filling the relevant columns, else the bidder is liable to be rejected for this tender. Bidders are allowed to enter the Bidder Name and Values only )
NUMBER # | TEXT # | NUMBER # | TEXT # | NUMBER # | NUMBER | NUMBER # | NUMBER # | NUMBER #
Sl. No. | Item Description | Quantity | Units | UNIT RATE In Figures To be entered by the Bidder in Rs. P | GST in Rs. P (Col. 5 x % of GST) | Total Unit Rate with GST (Col. 5+6) | TOTAL AMOUNT Without Taxes in Rs. P (Col. 3 x 5) | TOTAL AMOUNT With Taxes in Rs. P (Col. 3 x 7)
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9
A | CIRCUIT CUM POINT WIRING
The rates for all point wiring items shall also include supplying and fixing of the following:
1 | Conduits, conduit accessories, brass bushes and other fittings.
2 | Approved GI saddles and grouting the same for exposed conduit work.
3 | 1.2 mm thick Outlet boxes and junction box.
4 | All fixing accessories such as clips, brass screws etc.
5 | All work necessary for wiring a point circuit of any length from the Final Distribution Board to connector via switch and shall include the circuit wiring also except where identified.
6 | Embedding conduits and accessories in walls and floors etc. during construction and / or cutting chases (with chase cutting machine) and making good the same as necessary in the case of concealed conduit work.
7 | Switch, socket outlet and necessary blank plates wherever required.
8 | FRLS copper conductor stranded flexible FRLS wire of Green colour or Green colour with yellow band for earthing of fixtures, outlet boxes and third pin of socket outlet.
9 | Repainting of outlet boxes and juction boxes where ever damaged.
10 | All wires shall be IS approved, 1100 volt grade, stranded flexible FRLS.
11 | All sockets shall be shuttered type with earth terminal.
12 | Suitable rating of plugs top shall also be provided within the quoted rates for all polycarbonate splash proof socket outlets.
13 | Separate neutral and earthing wire shall be provided for each circuit.
14 | Lighting and power circuit to be kept separate.
1 | Wiring for the following light points with 2.5 sq.mm (including circuit wiring) PVC insulated FRLS copper conductor 1100 volts grade stranded flexible wires of approved make in Surface/ concealed 25 mm dia PVC. conduit including providing and fixing of 6 amps single pole rocker operated flush mounted switch of approved quality, colour, make and design in 1.2 mm thick GI box and earthing of fixtures and the outlet box with 2.5 sq.mm PVC insulated FRLS copper conductor stranded flexible wire.
a | Primary points | 7 | Pts | 0 | 0 | 0 | 0 | 0
b | Loop points | 15 | Pts | 0 | 0 | 0 | 0 | 0
2 | Wiring of 240 volts single phase, 6/16 Amp switched socket outlet with 2 x 4 + 1 x 2.5 Sq mm. 1100V FRLS PVC insulated copper multistranded conductor wires in PVC conduit including providing and fixing of 6 pin 16 Amps modular plate type switched & socket with the GI box, earthing of 3rd pin with PVC insulated green colour 2.5 Sq mm. 1100V copper wire, complete with all accessories as required. | 3 | Pts. | 0 | 0 | 0 | 0 | 0
3 | Wiring for light point as in item No. A-1 above but controlled by SPMCB provided in the DB. (Cost of MCB not to be included here).
a | Primary points | 2 | Pts.
b | Loop points | 3 | Pts.
B | CABLES AND CABLE TRAYS
The rate shall also include the following :
1 | Providing and fixing junction boxes with covers including painting where ever required.
2 | Providing all fixing accessories such as clamping devices nuts, bolts and screws.
3 | Wherever the cables are of copper and bus bars of copper bimetallic lugs shall be used.
4 | All cable shall be laid with one diameter gap.
5 | All cables shall be IS approved.
6 | Double compression glands with earthing provision.
7 | Fire retardent paint one meter on both side of wall penetration and at termination as per specifications.
8 | Burried LT cables to be laid atleast 750 mm below ground.
1 | Supply, laying & testing of of following 1100 volt grade XLPE Cu conductor armoured cables as per specification in existing , cable trays, ducts, over bed of sand, clamped to wall with suitable clamps including, saddles fixing bolts, connecting testing and commissioning.
1.1 | 4 X 6 sq. mm + 2 X 6 sq. mm earth wire | 50 | RM | 0 | 0 | 0 | 0 | 0
2 | Supply and fixing of perforated type G.I. cable trays of the following sizes including providing 2 No. 25 x 25 x 4 mm GI angle suspenders at 1800 mm C/C as per specifications..
2.1 | 100 mm x 50 mm x 1.6 mm thick | 50 | RM | 0 | 0 | 0 | 0 | 0
3 | Supply and laying of SS Raceway with cover with galvanished coating and Pre-coating of the following sizes.
3.1 | 50 mm x 50 mm | 100 | RM | 0 | 0 | 0 | 0 | 0
C | FINAL DISTRIBUTION BOARDS
Note:- Contractor shall provide the number of outgoings with SP MCB as descri bed in the items along with considering extra space for DP RCCB for each phase. For example, 4Way TPN, the SP MCB output shall be 4 nos plus 1 no. DP RCCB.
1 | Supply, installation, testing and commissioning of the following FDB's fabricated out of 16/18 guage thick CRCA sheet steel, double door lockable construction, powder coated with approved shade and partitions to segregate phases. recessed in wall or surface mounted final distribution boards complete with inter connecting wires of proper guage, aluminium coated copper thimbles and with the circuit identification tags. The DB shall be suitable for taking cable/conduit as incoming/outgoing. Incomer cable must be terminated into DB by providing cable gland as per approved make. All MCB to be C Curve unless specified otherwise & of 10 KA breaking capacity. Each panel shall have its laminated circuit diagram. Final distribution board are as per the following descriptions:
Note:- Contractor shall provide the number of outgoings with SP MCB as descri bed in the items along with considering extra space for DP RCCB for each phase. For example, 4Way TPN, the SP MCB output shall be 4 nos plus 1 no. DP RCCB.
1.1 | 8 way TPN DB, 18 Nos. 10/16/20 A SP MCB’s per phase with 3 Nos. 25 A DP RCCB’s of 30 mA leakage current and 1 No. 40 A 4P MCB as incomer with separate neutral link for each phase. | 1 | Nos. | 0 | 0 | 0 | 0 | 0
1.2 | 6 way TPN DB, 12 Nos. 10/16/20 A SP MCB’s per phase with 3 Nos. 25 A DP RCCB’s of 30 mA leakage current and 1 No. 40 A 4P MCB as incomer with separate neutral link for each phase. | 3 | Nos. | 0 | 0 | 0 | 0 | 0
D | RECEIVING, STORING, INSTALLATION OF LIGHTING FIXTURES
Note:- The selection of fixtures shall be as per client/ architect and supply for the same shall be in owner scope and to be designed by lighting consultants. The same has not been considered here.
1 | The rates shall include all components that may be required to make the installation complete in all respects such as :
a | All lamps and control gears.
b | Internal wiring between accessories.
c | Earthing terminal.
d | Complete provision for installation.
e | Wires for connecting the fixtures to the point through connector block.
f | All metal blocks to serve as base of fixtures.
g | Bonding with earth wires.
2 | Drilling holes in supports wherever required.
3 | Fixing clamps, GI bolts and nuts, brass screws, saddles, rawl bolts and other fixing accessories as required.
4 | Testing of all fixtures & fans bfore and after installation.
5 | Rates for Installation of light fixture are inclusive of any PVC/G.I flexible conduit if required.
6 | Receiving, storing , installation, testing & commissioning of following type of light fixtures as per schedule of fixtures, drawings & specifications. (Fixtures shall be with required dimming provision as per its requirement)
a | 1X34W Surface Mounted Grid ceiling Light Fixture | 12 | Nos | 0 | 0 | 0 | 0 | 0
b | 1X15W Surface Mounted Grid ceiling Light Fixture | 4 | Nos | 0 | 0 | 0 | 0 | 0
c | 1X18W Surface Mounted ceiling Light Fixture | 10 | Nos | 0 | 0 | 0 | 0 | 0
E | MISCELLANEOUS ELECTRICAL ITEMS
1 | Supply, installation, testing and commissioning of 10 kVA UPS, 1 phase (230 V + 15%) Volts input & 1 phase output (230 V + 1%), 50 Hz, 100% IGBT inverter & converter, Input harmonic Current THD 3% typical at 100% load, 6% maximum at 50% load, Unity power factor, AC-AC efficiency >=95%, paralleling up to 04 Unit and 30 min battery backup (VAH = 8064) with 12 V SMF VRLA batteries for UPS along with battery rack & Interconnecting cables. Quoted price shall be inclusive of approved rating single core copper conductor cable connecting UPS and batteries.
| 10 kVA | 1 | Set | 0 | 0 | 0 | 0 | 0
2 | Supplying & Fixing of 12 core full loaded LIU should be of 1U size and 19” rack-mountable encloser.LIU should be complete with 9/125μm multi mode pigtails.LIU should be complete with splicing tray and other standard accessories.LIU should be loaded with SC/LC-type adopter and couplers.LIU should be of ROHS compliant. | 1 | Unit | 0 | 0 | 0 | 0 | 0
3 | Supplying & Fixing of Fiber Optic Cable ISO/IEC-11801-OM3 50μ Duplex, LSZH,Shall be Duplex Multi Mode Fiber Optic OM3 50μ,Shall support network line speeds up to 10 Gbps.Shall have LC-LC Connector connectors at the ends complete in all respect. | 90 | Mtr | 0 | 0 | 0 | 0 | 0
4 | Supplying & Laying of CAT 6 Cable should be unshielded twisted pair cabling system, TIA / EIA 568-C.2 Category 6 Cabling system.Network support should be ultra high speed data networks such as Gigabit Ethernet (1000 Base-T and 1000 Base-TX) and beyond.Cable should be ETL Verified, UL Listed and UL channel verified- all three certificates are mandatory. Conductors type should be 23 AWG solid bare copper.Frequency tested should be up to 600 MHz minimum.Impedance should be 100 ± 15 Ohms.Propagation delay should be 535ns/100m @250MHz.cable should be RoHS compliant. Cable Qty. conisidered for ( DATA +CCTV+ Voice) | 640 | Mtr | 0 | 0 | 0 | 0 | 0
5 | S/F of fire extinguishers welded SS304 Body ABC type 6 kg capacity (ISI maked IS:2878 & TAC approved) complete with initial charge & wall bracket along with supply of all material and labour for proper completion of work. MAKE: KALPEX/ MINIMAX/ SAFEX/ KANEX | 4 | Mtr | 0 | 0 | 0 | 0 | 0
6 | S/F of fire extinguishers seamles MS Body CO2 type 4.50 kg capacity (ISI maked IS:2878 & TAC approved) complete with initial charge & wall bracket along with supply of all material and labour for proper completion of work. MAKE: KALPEX/ MINIMAX/ SAFEX/ KANEX | 4 | Nos. | 0 | 0 | 0 | 0 | 0
7 | S/F of fire extinguishers seamles MS Body CO2 type 4.50 kg capacity (ISI maked IS:2878 & TAC approved) complete with initial charge & wall bracket along with supply of all material and labour for proper completion of work. MAKE: KALPEX/ MINIMAX/ SAFEX/ KANEX | 4 | Nos. | 0 | 0 | 0 | 0 | 0
8 | S/F of fire extinguishers seamles MS Body Clean Agent type 6 kg capacity (ISI maked IS:2878 & TAC approved) complete with initial charge & wall bracket along with supply of all material and labour for proper completion of work. MAKE: KALPEX/ MINIMAX/ SAFEX/ KANEX | 1 | Nos. | 0 | 0 | 0 | 0 | 0
9 | Making the connection of Existing Electrical panels/DB to proposed db necessary switchgear and wire including cut in chases, conduit and laying in conduit/surface etc. whatever required at site and repair the wall with plaster, concrete whatever required at site complete in all respect nothing will be paid separately. | 1 | Job | 0 | 0 | 0 | 0 | 0
10 | Supply of IP20 linear 120mm wide, 33mm width suspended fitting made of extruded aluminium housing, Opal diffuser connected with customised grey coloured frame. Fixture should have minimum efficacy at System level (Not Chip Level) >100lumens/watt and a minimum system lumen output of >120 lumens and maximum system wattage of 147W. Luminaire should have Life of 50000hrs@L70B50 Lumen maintenance, CCT up to 4000K, CRI >80, PF >0.95, THD<10% and an operating Voltage Range of 140 - 270 Internal Surge Protection 4KV. The fixture should comply with the parameters as per IS10322. The LED driver should comply to IEC61000-3-2 ed.3.2, 2009 for Harmonics, IEC61347 -2 -13, 2006 in Conjunction with IEC61347-1 ed.2.0, 2007 for Electrical Safety, IEC62384 ed.1.1, 2011 for performance and IEC61547 ed.2.0, 2009, CISPR- 15 for EMI. Manufacturer shall have inhouse lab approved by NABL or ministry of science of govt of India. LM 79 and LM80 reports need to be submitted from a NABL/UL accredited lab to verify above parameters. Including 3 core 1.5 sq.mm. Similar to Signify Flatline with Frame or Equivalent in LT/Regent | 1 | Nos. | 0 | 0 | 0 | 0 | 0
11 | Making the connection of Existing server Hub to proposed server with necessary items, software and wire including cut in chases, conduit and laying in conduit/surface etc. whatever required at site and repair the wall with plaster, concrete whatever required at site complete in all respect nothing will be paid separately. | 1 | Job | 0 | 0 | 0 | 0 | 0
|  |  |  | 0 | 0 | 0 | 0 | 0
F | ACOUSTICAL TREATMENT |  |  | 0 | 0 | 0 | 0 | 0
1 | Providing and Fixing of 24mm WPC wall panelling with ND40 Screw fixed @ 200mm on GI studd of 50 x 50mm making a grid of 610 x 610mm c/c.The frame is to be made in proper line after leveling. The work to be done complete as per the design & instructions of architect including all accessories/ hardware required. Make: Megastar, Leben, Arbor | 448 | sqft | 0 | 0 | 0 | 0 | 0
2 | Providing and Fixing of 12mm Thick Acoustic panels with square ore beveled edge, the apnels are manufactured from 100% polyethylene terephthalate have density of 18 kg/m3, panels should be fire resistant as per B1 Class A. The panel to be glued over 8 mm thick perforated ply fixed over GI framework made of GI studs of 48x36x34mm, .5mm thick matching ceiling section. The GI framing to be centre filled with 50mm thick 1000GSM polyester wadding. The panel should be pasted to be the perforated ply with SH/SRS adhesive. The work to be done complete as per the design & instructions of architect including all accessories | 740 | sqft | 0 | 0 | 0 | 0 | 0
3 | Providing and fixing partition upto ceiling height consisting of G.I. frame and required 12mm bison board, including providing and fixing of frame work made of special section power pressed/ roll form G.I. sheet with zinc coating of 120 gms/sqm(both side inclusive), consisting of floor and ceiling channel 50mm wide having equal flanges of 32 mm and 0.50 mm thick, fixed to the floor and ceiling at the spacing of 610 mm centre to centre with dash fastener of 12.5 mm dia meter 50 mm length or suitable anchor fastener or metal screws with nylon plugs and the studs 48 mm wide having one flange of 34 mm and other flange 36 mm and 0.50 mm thick fixed vertically within flanges of floor and ceiling channel and placed at a spacing of 610 mm centre to centre by 6 mm dia bolts and nuts, including fixing of studs along both ends of partition fixed flush to wall with suitable anchor fastener or metal screws with nylon plugs at spacing of 450 mm centre to centre, and fixing of boards to both side of frame work by 25 mm long dry wall screws on studs, floor and ceiling channels at the spacing of 300 mm centre to centre. The boards are to be fixed to the frame work with joints staggered to avoi d through cracks, M.S. fixing channel of 99 mm width (0.9 mm thick having two flanges of 9.5 mm each) to be provided at the horizontal joints of two boards, fixed to the studs using metal to metal flat head screws, including jointing and finishing to a flu sh finish with recommended jointing compound, jointing tape, angle beads at corners (25 mm x 25 mm x 0.5 mm), joint finisher and two coats of primer suitable for board as per manufacture's specification and direction of engineer in charge all complete. Rockwool with thickness of 50mm having 96 kg density will be laid on existing grid for better insulation. | 400 | sqft | 0 | 0 | 0 | 0 | 0
4 | Providing & Fixing of Mineral Fiber Acoustical Suspended Ceiling System - PIN HOLE (BUTT / TEGULAR) EDGE TILES WITH REGULAR 24 mm EXPOSED GRID. The tiles should have Humidity Resistance (RH) of 85%, NRC 0.50, Light Reflectance >84% with Fire Resistance as per GB8624 B1 in module size of 600 X 600 X 15 mm as per the drawing and the work complete in all respects to the satisfaction of Engineer in-charge. | 882 | sqft | 0 | 0 | 0 | 0 | 0
5 | Providing and Fixing 20oz. Loop plie 2' x 2' carpet with precision tufted loop piles as underlay of 6mm thick PU foam fixed to existing levelled floor with syntheic adhesives as approved by the manufacturer. | 882 | sqft | 0 | 0 | 0 | 0 | 0
6 | Supply & Fixing of 75mm acoustic doors at site 75mm thick acoustic and sound reducing doors made with 2nd class Wooden Framework, infill in 24 kg/cum density resin bonded glass wool with 12mm commercial ply and 1mm thick laminate on both sides. Cost includes Sal wood Chowkhat ( Section size: 5'' × 3'') fixing acoustical seals, stainless steel ball bearing hinges, door closers, door stoppers and steel handles. | 4 | Nos | 0 | 0 | 0 | 0 | 0
7 | Providing and Fixing of 10' x 8' Window blinds thickness:0.02in(0.53mm), vacuum cleaning and/or gentle wiping with a sponge and mild soap. DO not soak, do not use any other solvents and do not rub. | 3 | Nos | 0 | 0 | 0 | 0 | 0
|  |  |  | 0 | 0 | 0 | 0 | 0
G | DOORS AND FLOOR WORK |  |  | 0 | 0 | 0 | 0 | 0
| Al Georgeon Bar Glass Doors |  |  | 0 | 0 | 0 | 0 | 0
1 | Providing & Fixing of Powder Coated slim Line ( 45mm x 25mm) Aluminium doors of Size 3'3" x 8'0" with Vertical Profiles,Horizontal Profiles,Georgian Bar Profiles AQ25, AQ25P, AQ25B, AQ25FD with 8mm Clear Toughened Glass Door Including Floor Spring, Lock, Handle and other requisite hardware (All Fittings of Ozone Make or Eqv) A - 16 , 17 & 14 | 4 | Nos | 0 | 0 | 0 | 0 | 0
| Carpet (CONFERENCE ROOM) |  |  | 0 | 0 | 0 | 0 | 0
2 | Providing and fixing Polyester And Synthetic Material Carpet Tiles flooring make in command centre etc. complete in all respect including fixing of 5 mm thick poly urethene foam rolls. Rates quoted should include cost of adhesives, fixing , cutting of carpet etc complete in all respects. (Basic price of Carpeting: Rs.150/- per Sft) | 800 | Sft | 0 | 0 | 0 | 0 | 0
| Floor tiles (CABINS AND CORRIDOR) |  |  | 0 | 0 | 0 | 0 | 0
3 | Providing and laying Vitrified tiles in floor with different sizes (thickness to be specified by the manufacturer), with water absorption less than 0.08% and conforming to IS:15622, of approved brand & manufacturer, in all colours and shade, laid with cement based high polymer modified quick set tile adhesive (water based) conforming to IS : 15477,in average 6 mm thickness including epoxy grouting of joints (LITECRETE or Eqv.), Including wastages etc complete of Tile sizes as below: |  |  | 0 | 0 | 0 | 0 | 0
| 600 x 1200mm / 800 x 800 (Basic Price of tile: Rs.160/- per Sft without GST) | 400 | Sft | 0 | 0 | 0 | 0 | 0
|  |  |  | 0 | 0 | 0 | 0 | 0
H | FURNITURE WORK |  |  | 0 | 0 | 0 | 0 | 0
1 | Work Surface-Made of 25mm Thick Pre-laminated twin board of E1-P2 grade and approved shadeconforming to IS-12823:1990, Edge banded with matching 2 mm thick PVC lipping.Plastic ABS access flap is provided for easy access to Wires and cables. Work top is available in various shapes as shown above. Understructure-It consist of 18mm Thick Pre-laminated twin board of E1-P2 grade and approved shade conforming to IS-12823:1990, Edge banded with matching 2 mm thick PVC lipping.Aluminium alloy 63400 - WP profile is used for connecting panels together. The product has a knock-down construction. Modesty Panel-Made of 18mm Thick Pre-laminated twin board of E1-P2 grade and approved shade conforming to IS-12823:1990, Edge banded with matching 2 mm thick PVC lipping. Powder coated accent metal strip provided below work surface to enhance aesthetics. It is made of 0.8mm CRCA as per IS 513,epoxy polyester powder coated (DFT 40-60 microns. Wire Management-An array of panels made of 0.8mm CRCA MS IS:513, epoxy polyester powder coated (DFT 40-60 microns) is used for flow of wires and cables. Provision to mount Anchor Roma 6 module plate is provided below worktop. Cutout on top with two piece injection moulded plastic part polymer component is fitted to pull out audio,video cables onto worktop and connect devices charger to power socket below worktop. 2 STR-1350 X 600 X 730 - ( 8 QTY) 1800W ST-1800 X 850 X 730 - (Qty -2) Makes- Goderej,Stanley ,Hayworth | 1 | Set | 0 | 0 | 0 | 0 | 0
| Supply, Assembling and Putting conference room chair of colour and specs as per given modle |  |  | 0 | 0 | 0 | 0 | 0
2 | High Back Chair Make:Kareena NXT-High Back | 2 | Set | 0 | 0 | 0 | 0 | 0
3 | Mid Back Chair Make:Kareena NXT-Mid Back | 34 | Set | 0 | 0 | 0 | 0 | 0
4 | Providing and Fixing of 20 mm thk Onyx Black Granite Countertop on furniture including all with necessary accessories nothing will be paid seperately | 6 | Sqm | 0 | 0 | 0 | 0 | 0
5 | Providing and fixing counter made of 3/4 inch thick prelaminated plyboard of size 8'-0"x4'-0" with provision for under counter cabinet + drawer unit with accessories with both side laminated in and out. | 20 | Sqm | 0 | 0 | 0 | 0 | 0
[7 empty] | 0 | 0
| Consultant Engineer |  |  |  | Seal & Signature of Contractor