## Sheet1
Item Wise BoQ
BoQ_Ver3.1 | Item Wise |  | INR and Other Currency
Tender Inviting Authority: Director, NIPGR, New Delhi
Name of Work:Replacement of existing Split ACs installed in old tissue culture labs at NIPGR Campus, New Delhi.
Contract No: NIPGR/Engg./5/8(2)/2024-25
Name of the Bidder/ Bidding Firm / Company :
PRICE SCHEDULE (This BOQ template must not be modified/replaced by the bidder and the same should be uploaded after filling the relevant columns, else the bidder is liable to be rejected for this tender. Bidders are allowed to enter the Bidder Name and Values only )
(This BOQ template must not be modified/replaced by the bidder and the same should be uploaded after filling the relevant columns, else the bidder is liable to be rejected for this tender. Bidders are allowed to enter the Bidder Name and Values only )
NUMBER # | TEXT # | NUMBER # | TEXT # | NUMBER # | NUMBER | NUMBER # | NUMBER # | NUMBER #
Sl. No. | Item Description | Quantity | Units | UNIT RATE In Figures To be entered by the Bidder in Rs. P | GST in Rs. P (Col. 5 x % of GST) | Total Unit Rate with GST (Col. 5+6) | TOTAL AMOUNT Without Taxes in Rs. P (Col. 3 x 5) | TOTAL AMOUNT With Taxes in Rs. P (Col. 3 x 7)
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9
PART-A
OUTDOOR UNIT'S
Supply of Modular type outdoor units, with all Scroll Inverter compressors (Copper winding) for cooling and heating application. The unit above 14HP must run with two no's of Inverter compressors (auto on/off loading) , Microprocessor based Controller, Top Discharge type along with the same shall have a minimum COP of 4.2 to 4.6 at AHRI condition and EER not less than 6.5. All inverter capacity controlling compressors of same OEM and are suitable for 380~415 volts. All ODU units must be fully charged with R-410A, Anti Corrosive coating , Vibration Isolators and must be equipped with Auto Clean Technology in which after every 60 Days condenser fan reverse the rotation to clean dust for better efficiency. The Outdoor PCB should have the technology to be cooled by refrigerant. Outdoor units must have a wide operation range from(-5◦ C to 55◦ C).
1.1 | 22 HP (Heating & Cooling) | 2 | Nos | 0 | 0 | 0 | 0 | 0
1.2 | 10 HP (Heating & Cooling) | 1 | Nos | 0 | 0 | 0 | 0 | 0
2 | INDOOR UNIT'S
Supply, of Indoor units equipped with pre-filter, fan section with suitable static fan, multispeed motor, coil section with DX coil,outer cabinet, drain pan, insulation, pipe connections, etc. of various capacities as per specifications.
2.1 | 3 TR - 4 Way Cassett | 14 | Nos | 0 | 0 | 0 | 0 | 0
2.2 | 2 TR - Hi Wall Split | 1 | Nos | 0 | 0 | 0 | 0 | 0
2.7 | ACCESSORIES.
2.8 | Wireless Remote | 15 | Nos | 0 | 0 | 0 | 0 | 0
2.9 | Y Joint for IDU | 12 | Nos | 0 | 0 | 0 | 0 | 0
2.1 | Centralized Remote | 1 | Nos | 0 | 0 | 0 | 0 | 0
3 | Installation Testing & Commissioning FOR OUTDOOR UNIT
3.1 | 22 HP (Heating & Cooling) | 2 | Nos | 0 | 0 | 0 | 0 | 0
3.2 | 10 HP (Heating & Cooling) | 1 | Nos | 0 | 0 | 0 | 0 | 0
4 | Installation Testing & Commissioning FOR INDOOR UNIT
4.1 | Cassette AC's 4 way & Hi Wall Unit
4.2 | 3 TR | 14 | Nos | 0 | 0 | 0 | 0 | 0
4.2 | 2 TR | 1 | Nos | 0 | 0 | 0 | 0 | 0
5 | ITC of Y Branch IDU
5.1 | Y Joint IDU | 12 | Nos | 0 | 0 | 0 | 0 | 0
6 | Refrigerant Piping for VRV / VRF System
6.1 | Supply & Fixing of COPPER REFRIGERANT PIPING of appropriate size and thickness as recommended by OEM, suction and discharge line complete with fittings, elbow, socket, brazing, flushing, Pressure testing with N2, vacuuming. nitrile rubber insulation of 19 mm thickness for gas line and 19 mm thickness & 13 mm for liquid line. Measurement of pipes individually. (Gas and liquid line) including bend and accessories etc. Copper Pipes Should handle Pressure upto 500 Psi.
6.2 | 28.58 mm OD ( insulation 19mm) | 40 | Mtr. | 0 | 0 | 0 | 0 | 0
6.3 | 22.2 mm OD ( insulation 19mm) | 30 | Mtr. | 0 | 0 | 0 | 0 | 0
6.4 | 19.05 mm OD ( insulation 19mm) | 50 | Mtr. | 0 | 0 | 0 | 0 | 0
6.5 | 15.88 mm OD ( insulation 19mm) | 30 | Mtr. | 0 | 0 | 0 | 0 | 0
6.6 | 12.7 mm OD ( insulation 19mm) | 50 | Mtr. | 0 | 0 | 0 | 0 | 0
6.7 | 9.52 mm OD ( insulation 13 mm ) | 200 | Mtr. | 0 | 0 | 0 | 0 | 0
6.8 | 6.4 mm OD ( insulation 13 mm ) | 10 | Mtr. | 0 | 0 | 0 | 0 | 0
7 | GI Cable tray with Cover, 200 mm x 50 mm x 1.6 mm thick with threaded Rod 8 mm, Anchor Fastener, Nut Bolt, Washer, Tie for top Covering Cable Tray, etc for ODU Unit along Civil work for Platform wherever required | 40 | Mtr | 0 | 0 | 0 | 0 | 0
8 | Condensate Drain Piping
8.1 | Supplying, installing and testing of hard PVC pipe (heavy duty- 10kg Pressure) with 9 mm thick nitrile rubber insulation (tube insulation) as per the approved shop drawings and specifications along with it accessories for hanging
8.2 | Hard PVC drain Pipe 32 mm , 10 kg with 9 mm thick Insulation | 90 | Mtr. | 0 | 0 | 0 | 0 | 0
9 | TRANSMISSION WIRING.
9.1 | Supply, laying, testing, and commissioning of the following size (Shielded) PVC insulated Copper Communication cable in PVC conduit of the following size on surface/recessed i/c clamping completely as required.- 3 core x 1.5 Sq mm
| 3C x 1.5 Sq mm Unarmoured (For Transmission) | 400 | Mtr. | 0 | 0 | 0 | 0 | 0
9.2 | Supplying and fitting the following size of perforated Galvanized Iron Cable Tray (150mm x 50mm x 1.6 mm thick) including bends and tee with perforation, in convenient sections, Anchor Fastener Thread Rod Nut bolt Washer joined with connectors, suspended from the ceiling with M.S. suspenders for Indoor Unit Power Supply. | 80 | Rmt | 0 | 0 | 0 | 0 | 0
9.3 | Supply and fixing 3C x 2.5 sq. mm. Copper Multi Stand Wire cable for Indoor Unit Power Supply. (Or as per the OEM recommendation to take the proper load) | 200 | Rmt | 0 | 0 | 0 | 0 | 0
9.4 | 4C x 10/16/25 sq. mm. Copper Multi Stand cable + 1.5 sq mm. for earth for outdoor Unit Power Supply and fixing from Electrical Panel to Outdoor Unit (Or as per the OEM recommendation to take the proper load) | 350 | Rmt | 0 | 0 | 0 | 0 | 0
10 | Providing and fixing 25 mm X 5 mm G.l. strip on the surface or in recess for connections etc. as required. | 40 | Rmt | 0 | 0 | 0 | 0 | 0
11 | Providing and fixing 6 SWG dia G.l. wire on the surface or in recess for loop earthing as required. | 180 | Rmt | 0 | 0 | 0 | 0 | 0
12 | Supply and installation of MS Outdoor unit stand with two coats paint, Outdoor stand mounted on Terrace area of library Including Rubber Pad. | 3 | Nos. | 0 | 0 | 0 | 0 | 0
Total in figures | [6 empty] | 0 | 0
Quoted Rate in Words
Sl. No. | Item Description | Quantity | Units | UNIT RATE In Figures To be entered by the Bidder in Rs. P | GST in Rs. P (Col. 5 x % of GST) | Total Unit Rate with GST (Col. 5+6) | TOTAL AMOUNT Without Taxes in Rs. P (Col. 3 x 5) | TOTAL AMOUNT With Taxes in Rs. P (Col. 3 x 7)
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9
PART-B
1 | Comprehensive Annual Maintenance Contract of the above VRV installation including all accessories. The CAMC cost shall include repair / replacement of all the equipment, spare and any other material required to make system functional. Agency shall provide undertaking from OEM that the equipment being supplied shall be able to run for 10 years and there spares shall be readily available when required.
| First year after expiry of DLP | 1 | Per year | 0 | 0 | 0 | 0 | 0
| Second year after expiry of DLP | 1 | Per year | 0 | 0 | 0 | 0 | 0
| Third year after expiry of DLP | 1 | Per year | 0 | 0 | 0 | 0 | 0
| Forth year after expiry of DLP | 1 | Per year | 0 | 0 | 0 | 0 | 0
| Fifth year after expiry of DLP | 1 | Per year | 0 | 0 | 0 | 0 | 0
Total in figures | [6 empty] | 0 | 0
Quoted Rate in Words
| Controller of Administration |  |  |  | Seal & Signature of Contractor