## Sheet1
Item Wise BoQ
BoQ_Ver3.1 | Item Wise |  | INR and Other Currency
Tender Inviting Authority: Director, NIPGR, New Delhi
Name of Work:Provision of underground RCC water storage tanks of 50,000 litres capacity in Experimental Field at NIPGR Campus, New Delhi.
Contract No: NIPGR/Engg./7/5(1)/2025-26
Name of the Bidder/ Bidding Firm / Company :
PRICE SCHEDULE (This BOQ template must not be modified/replaced by the bidder and the same should be uploaded after filling the relevant columns, else the bidder is liable to be rejected for this tender. Bidders are allowed to enter the Bidder Name and Values only )
(This BOQ template must not be modified/replaced by the bidder and the same should be uploaded after filling the relevant columns, else the bidder is liable to be rejected for this tender. Bidders are allowed to enter the Bidder Name and Values only )
NUMBER # | TEXT # | NUMBER # | TEXT # | NUMBER # | NUMBER | NUMBER # | NUMBER # | NUMBER #
Sl. No. | Item Description | Quantity | Units | UNIT RATE In Figures To be entered by the Bidder in Rs. P | GST in Rs. P (Col. 5 x % of GST) | Total Unit Rate with GST (Col. 5+6) | TOTAL AMOUNT Without Taxes in Rs. P (Col. 3 x 5) | TOTAL AMOUNT With Taxes in Rs. P (Col. 3 x 7)
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9
1 | Earth work excavation over areas in foundation of tank, pits, trenches etc. in all soils , soft and hard rock upto depth of 3.0mtrs including shoring & dewatering if necessary, dressing the sides, trimming, ramming and preparing the bed for foundation & refilling All around the foundation/ tank (after testing) with selected excavated earth, in layers not exceeding230mm. thick watering consolidation and disposing of the surplus earth within a distance of 500 M. etc.complete as per specifications, drawings including spreading,IeveIfing the surplus disposed of earth in required grade /profile & as directed by tInstitute.
| a) all Kind of Soils | 8 | Cum | 0 | 0 | 0 | 0 | 0
| b)Ordinary Rock | 24 | Cum | 0 | 0 | 0 | 0 | 0
| c) Hard Rock( blasting prohibited) | 16 | Cum | 0 | 0 | 0 | 0 | 0
2 | Cement concrete 1:3:6 in foundation plinth, supports using graded stone aggregate of 20mm. maximum size including necessary form work, machine ixing, transporting, placing in position consolidation, finishing, curing etc.in all works upto plinth level all complete as per specifications as directed by Institute | 6 | Cum | 0 | 0 | 0 | 0 | 0
PART-B STRUCTURAL WORKS
a) All RCC shall be controlled concrete unless otherwise specified and shall be carried out strictly in accordance with the drawings and specifications.
b) The rates for RCC works shall be exclusive of cost of reinforcement and form work unless otherwise mentioned.
c) All coarse aggregate to be 20mm. maximum size and uniformly graded
unless otherwise mentioned.
d) The controlled concrete grade M-20 shall be water tight controlled concrete and if any defective work is found during the testing of the tank , the contractor has to set right the same with pressure cement grouting etc. to the satisfaction of the Engineer in Charge at his own cost.(No extra payment will be admissible on this account)
and if any defective work is found during the testing of the tank , the contractor has to set right the same with pressure cement grouting etc. to the satisfaction of the Engineer in Charge at his own cost.(No extra payment will be admissible on this account) or all RCC items, the rates quoted shall include the following without any cost to the Department.Spacers to maintain clear cover for reinforcement. Drip moulds.
iii) Fixing at correct level and in proper alignment the inserts, pipe sleeves,
pipe bends, fan hooks, other pipe specials etc. if supplied by the Department
unless otherwise specified.
iv) slabs in panels of 150mm width ,construction joints etc.
v} f'orming of curvatures , roundings slopes, chamfers,notches,cornices etc. unless olher wise mentioned.
vi ) all concrete surfaces shall be closely hacked as per specifications and as
directed by the Engineer in Charge , whereever required.
vii} extra cement required for grouting and cement concrete , if any
viii) testing of water tightness and set right the defects if any
ix} cleaning of water tank after test/before handing over to be done to the
entire satisfaction of the engineer in charge.
3 | Reinforced cement concrete of at all floors and levels using graded stone aggregate of 20mm. and down graded including machine mixing, conveying, placing in position, mechanical consolidation, finishing, curing, scaffolding , dewatering if necessary and testing the concrete” for water tightness,rectification of defects if any including pressure cement grouting if required etc. complete all as per drawing & specifications, but excluding the cost of form work and steel rein- forcement (which shall be paid under relevant item) etc all complete as per direction of Institute.
3a) | Concrete of 1:1.5:3( 1 Cement :1.5 Coarse Sand :3 graded stone nominal size for Foundation , raft,walls, beams, slabs etc | 25 | Cum | 0 | 0 | 0 | 0 | 0
4 | Providing, erecting, fixing in position striking /removing and cleaning steel /timber shuttering & centering for form work in super structure at all level & locations for all shapes with chamfers, splays ,keys, wedges, rails ,bracings,props, brackets, cutting holes for pipes etc.including necessary staging for all clear story height providing & applying approved form oil on all surfaces of form work coming in contact with concrete including staging for all clear story height providing & applying approved form oil on all surfaces of form work coming in contact with concrete including close hacking of all exposed concrete work after removal of form work, all materials, labour dewatering if necessary etc. complete as per specifications, drawings & as directed by the Institute (Area of form work in contact with concrete shall only to be measured for payment & stop boards for construction joints will not be measured for payment)
| a) In raft slab, raft beam etc. | 10 | Sqm | 0 | 0 | 0 | 0 | 0
| b)ln coIumns,waIls | 125 | Sqm | 0 | 0 | 0 | 0 | 0
| c) In beams. slabs etc. | 30 | Sqm | 0 | 0 | 0 | 0 | 0
5 | Reinforcement for RCC work at contractor's own cost including supplying,delivering and storing of various diametres as required at site of work transporting, decoiling, straightening, cutting, bending, placing in position at all depths, locations levels and binding with 18- 20 gauge,soft drawn annealed steel binding wire complete as per specifications and drawings. (Cost of binding wire shall be borne by contractor and binding wire shall not be measured for payment) etc all complete as per direction of Institute.
| Thermo mechanical Treatment | 1400 | Kg | 0 | 0 | 0 | 0 | 0
Part-C : General Finishing Works
6 | Providing patented cement based waterproofing treatment from outside to tank raft slab and walls, basement, trenches and underround structures during construction, consisting of a waterproofing layer over cement concrete 1:3:6 bedding finished with 20mm thick well pointed in the joints with cement and approved waterproofing compound as per manufacturer's specifications and continuing the treatment after completion of floor slab and side wall on the outer face of walls and upto a height of 500mm above the adjacent ground level. The total thickness of waterproofing treatment shall be about 75mm for floors and about 35 to 40mm for walls etc all complete as per direction institute.
6a) | a) for floors | 22 | Sqm | 0 | 0 | 0 | 0 | 0
6b) | b) for walls | 60 | Sqm | 0 | 0 | 0 | 0 | 0
Note : - I) the measurement for payment shall be as per actual area covered by the treatment
ii) A working space of about 600mm shall have to be provided in the excavation separately for treatment of exterior faces of walls and will be measured under relevant item.
iii) The cost of cemenf concrete 1:3:6 is not included in this and is to be catered for measurement seperately in the relevant item.
7 | Providing and fixing 40/50mm dia G.I. Pipes spout of required length including cutting the pipes to the required length,making holes in the RCC structure or brick work, reinstating the same to the original condition including using water proofing compound,curing etc complete all as directed by Institute & as shown in the drg. | 3 | Metre | 0 | 0 | 0 | 0 | 0
8 | Providing orange colour safety foot rest of minimum 6mm thick plastic encapsulated as per IS : 10910 on 12 mm dia steel bar conforming to IS: 1786 having minimum cross section as 23mmx 25mm and over all minimum length 263mm and width as 165mm with minimum 112mm space between protruded legs having 2 mm tread on top surface by ribbing or chequering besides necessary and adequate anchoring projections on tail length on 138mm as per standard drawing and suitable to with stand the bend test and chemical resistance test as per specifications and having manufacture's permanent identification mark to be visible even after fixing, including fixing with 30“20“15cm cement concrete block 1:3:6(1 cement :3 coarse sand :6 graded sone aggregate 20mm nominal size) complete as per design etc all complete as per direction of Institute. | 12 | Each | 0 | 0 | 0 | 0 | 0
Special Note :- All Water proffing work.
a) The contractor shall test (he surface where water proofing treatment provided for bone dry condition by filling up with water. No wet patches or leaks shall appear on the surrounding wall or under side of the slab.
9 | Providing and laying 50mm G.I. pipes complete with G.I. fittings ( socket, union, elbow etc) and two nos butterfly valves of 50mm dai including trenching and refilling etc. from as per requirement at site all complete as per direction of Institute. | 10 | Mtr | 0 | 0 | 0 | 0 | 0
10 | SITC of armered cable of 2.5sqmm x4core copper cable with earthing to be laid in MS conduit from the underground tank to main panel along road with thimbles etc all complete as per direction of Institute. | 15 | Mtr | 0 | 0 | 0 | 0 | 0
11 | Providing and laying integral crystalline slurry of hydrophic in nature for waterproofing treatment to the RCC structure like retaining walls of the basement, water tanks, roof slabs, podiums,reservo ir sewage & water treatment plant tunnels.s ub way etc prepared by mixing in the ratio of 5:2 (5 parts integral crystalline slurry" 2 parts water) for vertical surfaces and 3:1 ( 3 part integral crystall ine slurry: 1 part water) for horizontal surfaces and applying the same from negative( internal ) siede with the help of synthetic finbre brush. The matter shall be meet the requirements as specified in ACI-212-3R-2010 i. e by reducing phe ermteability of Concrete by more than 90% compared with control concrete as per DIN 1048 and resistant toydrostatic 1h6 bar hydrasatic prehe stsure on negative side. The crystalline slurry shall be capable of self healing of crakes up to width of 0.5mm. The work shall be carried out all complete as per specification and direction of the Institute.
11a) | For Vertical Surface two coats @0.7 kg/per sqm. | 60 | Sqm | 0 | 0 | 0 | 0 | 0
11b) | For Horizontal Surface one coat@1.11 kg/persqm | 22 | Sqm | 0 | 0 | 0 | 0 | 0
12 | 11.3 Cement concrete flooring 1:2:4 (1 cement : 2 coarse sand : 4 graded stone aggregate) finished with a floating coat of neat cement, including cement slurry, but excluding the cost of nosing of steps etc. complete as per direction of Institute.
12a) | 40 mm thick with 20 mm nominal size stone aggregate sqm 545.00 | 16 | Sqm | 0 | 0 | 0 | 0 | 0
13 | Supply & Installation of Mono block pump set (Pump and motor) with specifications:-2 HP Single phase mono block pump set, RPM not less than 2500, Power rating 230v, pump delivery size not less than 40mm x suction size 50mm, Head range not less than 20 meter to 40 meter, Discharge not less than 300 LPM voltage 230V ,Single phase star delta panel starter with appropriate relay. The make of pump preferably be of Kirlosker, Crompton, Grand force etc. including the following GI fittings for each pump of 2HP monoblock etc all complete as per direction of Institute. | 2 | Nos | 0 | 0 | 0 | 0 | 0
1. GI Elbow 50/40mm 3 Nos
2. GI Socket 50 /40mm 1 Nos
3. GI Reducer socket 40x50 mm 2 Nos
4. GI Union 50/40 mm 2 Nos
5. GI Reducer Socket 50x 40 mm 2 Nos
6. GI Union 50/40 mm 2 Nos
7. GI Tee 50/40mm 2 Nos
8. GI BReducer Elbow 50x40 mm 2 Nos
9. GI Flange 50/40 mm 2 Nos
10. Brass Wheel Valve 50/40 mm 3 Nos
11. Brass Non Return valve 50/40 mm 2 Nos
12. Single phase starter 01 No with panel.
14 | Demolishing R.C.C. work manually/ by mechanical means including stacking of steel bars and disposal of unserviceable material within 50 metres lead as per direction of Institute | 4 | Cum | 0 | 0 | 0 | 0 | 0
15 | Demolishing brick work manually/ by mechanical means including stacking of serviceable material and disposal of unserviceable material within 50 metres lead etc all complete as per direction of Institute.
15a) | In cement mortar | 10 | Cum | 0 | 0 | 0 | 0 | 0
16 | Disposal of building rubbish / malba / similar unserviceable, dismantled or waste materials by mechanical means, including loading, transporting, unloading to approved municipal dumping ground or as approved by Institute., beyond 50 m initial lead, for all leads including all lifts involved. | 14 | Cum | 0 | 0 | 0 | 0 | 0
17 | Providing anfd Fixing in position Circular shape precast RCC manhole cover and frame H.D.20(600mm dia) on top of slab at approved location etc all complete as per direction of Institute. | 2 | Each | 0 | 0 | 0 | 0 | 0
Total in figures | [6 empty] | 0 | 0
Quoted Rate in Words
| Controller of Administration |  |  |  | Seal & Signature of Contractor