## Sheet1
Item Wise BoQ
BoQ_Ver3.1 | Item Wise |  | INR and Other Currency
Tender Inviting Authority: Director, NIPGR, New Delhi
Name of Work:Providing Ductable Air Conditioner in the Project Server Room at NIPGR Campus, New Delhi.
Contract No: NIPGR/Engg./5/2/2025-26
Name of the Bidder/ Bidding Firm / Company :
PRICE SCHEDULE (This BOQ template must not be modified/replaced by the bidder and the same should be uploaded after filling the relevant columns, else the bidder is liable to be rejected for this tender. Bidders are allowed to enter the Bidder Name and Values only )
(This BOQ template must not be modified/replaced by the bidder and the same should be uploaded after filling the relevant columns, else the bidder is liable to be rejected for this tender. Bidders are allowed to enter the Bidder Name and Values only )
NUMBER # | TEXT # | NUMBER # | TEXT # | NUMBER # | NUMBER | NUMBER # | NUMBER # | NUMBER #
Sl. No. | Item Description | Quantity | Units | UNIT RATE In Figures To be entered by the Bidder in Rs. P | GST in Rs. P (Col. 5 x % of GST) | Total Unit Rate with GST (Col. 5+6) | TOTAL AMOUNT Without Taxes in Rs. P (Col. 3 x 5) | TOTAL AMOUNT With Taxes in Rs. P (Col. 3 x 7)
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9
1 | Supply of R410a Refrigerant type R11TR Ductable split unit with Indoor and outdoor units with Scroll Compressors, thermostat and all standard accessories etc. Indoor unit comprising of Ductable split air conditioners with indoor unit comprising of pre-filter, low noise Copper Coil with fan section, etc. complete. The fan for outdoor unit shall be selected for low noise and the motor etc. shall be housed in a powder coated casing. Indoor unit shall be acoustically treated and shall be controlled with remote based wired / wireless microprocessor intelligent system with single phase prevention, reverse phase protection etc. Outdoor units shall be provided with suitable size angle iron stand/wall mounting including PCC Foundation etc,. duly painted and as directed. (single circuit machine shall be supplied) | 2 | No. | 0 | 0 | 0 | 0 | 0
2 | Installation testing and commissioning of Ductable split ACs mentioned at item no.1 with initial charge of refrigerant, hardware’s, labor, tools etc to make system complete functional . | 2 | No. | 0 | 0 | 0 | 0 | 0
3 | Supply Installation Testing Commissioning of Hard drawn copper refrigerant piping suitable for R410 a refrigerant of suitable size as required and duly insulated with 19mm/13mm thick closed cell elastomeric insulation in tubing form inclusive of glass cloth nd UC treatment of following sizes with necessary cable tray (closed type) , supports, fittings, interconnecting the liquid and suction pipe lines between the air cooled interconnecting outdoor and indoor units with proper insulation. Isolating valves need to be provided to isolate compressor, strainers, sight glass and any other component requires maintenance. (The copper pipe shall be as per OEM standard and rates shall be quoted accordingly).
a. | 1-1/8" dia | 40 | RMT | 0 | 0 | 0 | 0 | 0
b. | 5/8" dia | 40 | RMT | 0 | 0 | 0 | 0 | 0
4 | Supply, installation, Testing Commissioning of factory fabricated GSS rectangular Ducting with 13mm insulation of nitrile rubber duly pasted inside the duct as per standards with splitters, bends vanes, elbows gasket, nuts, bolts, angle iron flanges, GI threaded down rods and slotted GI supports. The rates quoted must be included with insulation / accaustic of the duct connections which shall be accoustic insulation with armasound
a. | 24 G SWG | 30 | sqmt | 0 | 0 | 0 | 0 | 0
b. | 22 G SWg | 20 | sqmt | 0 | 0 | 0 | 0 | 0
5 | Supply and fixing of good quality standard Extruded Aluminum powder quoted supply air grill with collar damper as approved by the Banks engineer. | 3 | sqmt | 0 | 0 | 0 | 0 | 0
6 | Supply and fixing of Fire retardant canvas connections size as required at site. | 2 | nos | 0 | 0 | 0 | 0 | 0
7 | Supply and providing of armoured Control cabling with 6c x 1.5 sq.mm copper cable for controlling from indoor to outdoor along with all necessary fittings and accessories to make system functional | 45 | sqmt | 0 | 0 | 0 | 0 | 0
8 | Supply & Installation of Drain water piping with 32mm CPVC pipe with insulation and neccesary accessories to avoid condensation | 10 | rmt | 0 | 0 | 0 | 0 | 0
9 | Supply and installation of armoured power cabling of 4c x 16 sq.mm copper cable for power supply to the ductable AC from the main electrical DB of NIPGR including mcb , mccb , thimble , gland , casing and caping along with all necessary fittings and accessories to make system functional | 25 | rmt | 0 | 0 | 0 | 0 | 0
Total in figures | [6 empty] | 0 | 0
Quoted Rate in Words
| Controller of Administration |  |  |  | Seal & Signature of Contractor